## seamless pipes 1.0 in
Annex.02: Technical Specifications for RFT No.[DAM 22/02475]
Technical Specification of GI Seamless pipes - 2.5 in
Brand / Country of Origin
1 | Pipe information
1-1 | Standard | ASTM A53
1-2 | Grade | Grade B
1-3 | Type | S: Seamless pipe
1-4 | Weight class | [STD], STD: standerd weight
1-5 | Schedule Number | 40
1-6 | Surface Finishing | Hot dipped galvanized
1-7 | Maximum proportion of checmical elements(%) :
1-7-1 | Carbon | Grade B : 0.30 (C )
1-7-2 | Manganese | Grade B : 1.2
1-7-3 | Phosphorus | Grade B : 0.05
1-7-4 | Sulfur | Grade B : 0.045
1-7-5 | Copper (A) | Grade B : 0.4
1-7-6 | Nicke (A) | Grade B : 0.4
1-7-7 | Chromium (A) | Grade B : 0.4
1-7-8 | Molybdenum (A) | Grade B : 0.15
1-7-9 | Vanadium (A) | Grade B : 0.08
1-8 | End finish | Plain or threaded or (threaded and coupled)
1-9 | Minimum tensile strength, min, psi [Mpa] | Grade B :60000 {415}
1-10 | Minimum yeild strength, min, psi [Mpa] | Grade B :35000 {240}
1-11 | Nondestructive Test (If it is requested)
1-12 | Weight per unit area of zinc coating(kg/m2) | The weight(mass) per unit area of zinc coating shall be not less than [0.55 kg/m2] as determined from the average results of the two specimens taken for test and not less than [0.49 kg/m2] for each of these specimens .
1-13 | Nominal size, inch | 1
1-14 | Outside Dia in[mm] : | 1.315[33.4]
1-15 | Specified wall thickness in[mm :
1-15-1 | for Plain-End Pipe | STD :0.133[3.38]
1-15-2 | for Threaded and Coupled Pipe , psi [Kpa] | STD :0.133[3.38]
1-16 | Nominal Weight (Mass) per unit Length lb/ft [kg/m]
1-16-1 | for Plain-End Pipe | STD : 1.68[2.5]
1-16-2 | for Threaded and Coupled Pipe | STD : 1.68[2.5]
1-17 | Hydrostatic pressure test :
1-17-1 | for Plain-End Pipe, STD psi [Kpa] | Grade B : 2500[17200]
1-17-2 | for Threaded and Coupled Pipe, STD psi [Kpa] | Grade B : 2500[17200]
1-18 | Pipe length (m) | STD : 6m
1-19 | Pipes NO. | Pipe Length
2 | Basic Threading and coupling Data
2-1 | Thread standard | ANSI Standard B 1.20.1
2-2 | Pipe thread type | Male, NPT
2-3 | Coupling thread type | Female, NPT
2-4 | Specified Outside Diameter, in. [mm] D | STD : 1.315[33.4]
2-5 | Number of Threads per Inch | STD : 8
2-6 | Approximate length of thread,in [mm] NL | STD : 11 1/2
2-7 | End of Pipe to Hand Tight Plane, in [mm] L1 | STD : 2 1/16[52]
2-8 | Effective Length, in. [mm] L2 | STD : 0.436[11.074]
2-9 | Total Length, in. [mm] L4 | STD : 0.7565[19.215]
2-10 | Pitch Diameter at Hand Tight Plane, in. [mm] E1 | STD : 1.0582[26.8783]
2-11 | Specified Outside Diameter, in. [mm] W | STD : 2.29627[58.32526]
2-12 | Hand Tight Stand-Off (Number of Threads) A | STD : 2.750[69.8]
213 | No. of Coupling | STD : 5 1/2
Note: | Male and female threads have to be provided with protectors to prevent any damage
(A) The total composition for these five elements shall not exceed 1.00 %.
(B) For each reduction of 0.01 % below the specified carbon maximum, an increase of 0.06 % manganese above the specified maximum will be permitted up to a maximum of 1.35%
(C) For each reduction of 0.01 % below the specified carbon maximum, an increase of 0.06 % manganese above the specified maximum will be permitted up to a maximum of 1.65 %

## seamless pipes 2.0 in
Annex.02: Technical Specifications for RFT No.[DAM 22/02475]
Technical Specification of GI Seamless pipes - 2.5 in
Brand / Country of Origin
1 | Pipe information
1-1 | Standard | ASTM A53
1-2 | Grade | Grade B
1-3 | Type | S: Seamless pipe
1-4 | Weight class | [STD], STD: standerd weight
1-5 | Schedule Number | 40
1-6 | Surface Finishing | Hot dipped galvanized
1-7 | Maximum proportion of checmical elements(%) :
1-7-1 | Carbon | Grade B : 0.30 (C )
1-7-2 | Manganese | Grade B : 1.2
1-7-3 | Phosphorus | Grade B : 0.05
1-7-4 | Sulfur | Grade B : 0.045
1-7-5 | Copper (A) | Grade B : 0.4
1-7-6 | Nicke (A) | Grade B : 0.4
1-7-7 | Chromium (A) | Grade B : 0.4
1-7-8 | Molybdenum (A) | Grade B : 0.15
1-7-9 | Vanadium (A) | Grade B : 0.08
1-8 | End finish | Plain or threaded or (threaded and coupled)
1-9 | Minimum tensile strength, min, psi [Mpa] | Grade B :60000 {415}
1-10 | Minimum yeild strength, min, psi [Mpa] | Grade B :35000 {240}
1-11 | Nondestructive Test (If it is requested)
1-12 | Weight per unit area of zinc coating(kg/m2) | The weight(mass) per unit area of zinc coating shall be not less than [0.55 kg/m2] as determined from the average results of the two specimens taken for test and not less than [0.49 kg/m2] for each of these specimens .
1-13 | Nominal size, inch | 2
1-14 | Outside Dia in[mm] : | 2.375[60.3]
1-15 | Specified wall thickness in[mm :
1-15-1 | for Plain-End Pipe | STD :0.154[3.91]
1-15-2 | for Threaded and Coupled Pipe , psi [Kpa] | STD :0.154[3.91]
1-16 | Nominal Weight (Mass) per unit Length lb/ft [kg/m]
1-16-1 | for Plain-End Pipe | STD : 3.66[5.44]
1-16-2 | for Threaded and Coupled Pipe | STD : 3.66[5.44]
1-17 | Hydrostatic pressure test :
1-17-1 | for Plain-End Pipe, STD psi [Kpa] | Grade B :
1-17-2 | for Threaded and Coupled Pipe, STD psi [Kpa] | Grade B :
1-18 | Pipe length (m) | STD : 6m
1-19 | Pipes NO. | Pipe Length
2 | Basic Threading and coupling Data
2-1 | Thread standard | ANSI Standard B 1.20.1
2-2 | Pipe thread type | Male, NPT
2-3 | Coupling thread type | Female, NPT
2-4 | Specified Outside Diameter, in. [mm] D | STD : 2.375[60.3]
2-5 | Number of Threads per Inch | STD : 8
2-6 | Approximate length of thread,in [mm] NL | STD : 11 1/2
2-7 | End of Pipe to Hand Tight Plane, in [mm] L1 | STD : 2 1/16[52]
2-8 | Effective Length, in. [mm] L2 | STD : 0.436[11.074]
2-9 | Total Length, in. [mm] L4 | STD : 0.7565[19.215]
2-10 | Pitch Diameter at Hand Tight Plane, in. [mm] E1 | STD : 1.0582[26.8783]
2-11 | Specified Outside Diameter, in. [mm] W | STD : 2.29627[58.32526]
2-12 | Hand Tight Stand-Off (Number of Threads) A | STD : 2.750[69.8]
213 | No. of Coupling | STD : 5 1/2
Note: | Male and female threads have to be provided with protectors to prevent any damage
(A) The total composition for these five elements shall not exceed 1.00 %.
(B) For each reduction of 0.01 % below the specified carbon maximum, an increase of 0.06 % manganese above the specified maximum will be permitted up to a maximum of 1.35%
(C) For each reduction of 0.01 % below the specified carbon maximum, an increase of 0.06 % manganese above the specified maximum will be permitted up to a maximum of 1.65 %

## seamless pipes 3.0in
Annex.02: Technical Specifications for RFT No.[DAM 22/02475]
Technical Specification of GI Seamless pipes - 3.0 in
Brand / Country of Origin
1 | Pipe information
1-1 | Standard | ASTM A53
1-2 | Grade | Grade B
1-3 | Type | S: Seamless pipe
1-4 | Weight class | [STD], STD: standerd weight
1-5 | Schedule Number | 40
1-6 | Surface Finishing | Hot dipped galvanized
1-7 | Maximum proportion of checmical elements(%) :
1-7-1 | Carbon | Grade B : 0.30 (C )
1-7-2 | Manganese | Grade B : 1.2
1-7-3 | Phosphorus | Grade B : 0.05
1-7-4 | Sulfur | Grade B : 0.045
1-7-5 | Copper (A) | Grade B : 0.4
1-7-6 | Nicke (A) | Grade B : 0.4
1-7-7 | Chromium (A) | Grade B : 0.4
1-7-8 | Molybdenum (A) | Grade B : 0.15
1-7-9 | Vanadium (A) | Grade B : 0.08
1-8 | End finish | Plain or threaded or (threaded and coupled)
1-9 | Minimum tensile strength, min, psi [Mpa] | Grade B :60000 {415}
1-10 | Minimum yeild strength, min, psi [Mpa] | Grade B :35000 {240}
1-11 | Nondestructive Test (If it is requested)
1-12 | Weight per unit area of zinc coating(kg/m2) | The weight(mass) per unit area of zinc coating shall be not less than [0.55 kg/m2] as determined from the average results of the two specimens taken for test and not less than [0.49 kg/m2] for each of these specimens .
1-13 | Nominal size, inch | 3
1-14 | Outside Dia in[mm] : | 3.500[88.9]
1-15 | Specified wall thickness in[mm :
1-15-1 | for Plain-End Pipe | STD :0.216[5.49]
1-15-2 | for Threaded and Coupled Pipe , psi [Kpa] | STD :0.216[5.49]
1-16 | Nominal Weight (Mass) per unit Length lb/ft [kg/m]
1-16-1 | for Plain-End Pipe | STD : 7.58[11.29]
1-16-2 | for Threaded and Coupled Pipe | STD : 7.68[11.35]
1-17 | Hydrostatic pressure test :
1-17-1 | for Plain-End Pipe, STD psi [Kpa] | Grade B : 2500[17200]
1-17-2 | for Threaded and Coupled Pipe, STD psi [Kpa] | Grade B : 2500[17200]
1-18 | Pipe length (m) | STD : 6m
1-19 | Pipes NO. | Pipe Length
2 | Basic Threading and coupling Data
2-1 | Thread standard | ANSI Standard B 1.20.1
2-2 | Pipe thread type | Male, NPT
2-3 | Coupling thread type | Female, NPT
2-4 | Specified Outside Diameter, in. [mm] D | STD : 3.500 [88.9]
2-5 | Number of Threads per Inch | STD : 8
2-6 | Approximate length of thread,in [mm] NL | STD : 3 3⁄16 [81]
2-7 | End of Pipe to Hand Tight Plane, in [mm] L1 | STD : 0.766 [19.456]
2-8 | Effective Length, in. [mm] L2 | STD : 1.2000[30.4800]
2-9 | Total Length, in. [mm] L4 | STD : 1.6337[41.4960]
2-10 | Pitch Diameter at Hand Tight Plane, in. [mm] E1 | STD : 3.38850[86.06790]
2-11 | Specified Outside Diameter, in. [mm] W | STD : 4.000 [101.6]
2-12 | Hand Tight Stand-Off (Number of Threads) A | STD : 5 1⁄2
213 | No. of Coupling
Note: | Male and female threads have to be provided with protectors to prevent any damage
(A) The total composition for these five elements shall not exceed 1.00 %.
(B) For each reduction of 0.01 % below the specified carbon maximum, an increase of 0.06 % manganese above the specified maximum will be permitted up to a maximum of 1.35%
(C) For each reduction of 0.01 % below the specified carbon maximum, an increase of 0.06 % manganese above the specified maximum will be permitted up to a maximum of 1.65 %